WattNodePulse Electric Energy Meter

Engineering Specifications

- The pulse energy meter shall make real energy measurements on single and multi-phase electrical circuits.

- The energy meter shall transmit the following readings:

  - Real positive energy pulses (watts) total for all phases

  - Real negative energy pulses (watts) total for all phases

  - Option for second total positive energy pulse output

  - Option for three individual phase pulse outputs

  - Option for Kh watt-hours per pulse constant

  - Option for pulse width

  - Other custom output capabilities are available as factory options

- The energy meter pulse outputs shall be optically isolated to 5000 Vac RMS

- The power meter shall derive operating power from its metering connections, and shall not require a separate power connection.

- Energy meter models must be available to directly accept voltage input at one of the following voltages: 120, 208-240, 277, 347 or 480 Vac (50 or 60Hz).

- The energy meter shall accept 0 to 0.333 Vac input from up to three current transducers.

- The energy meter shall be fitted with detachable terminal blocks for all wiring connections.

- The energy meter shall be calibrated with NIST traceable standards to an accuracy of 0.5% or better.

- The energy meter shall operate from –30°C to +55°C.

- The energy meter shall have dimensions not exceeding 6.1” x 3.4” x 1.5”.

- The energy meter shall be Continental Control Systems’ WattNode Pulse model.